## Requirements
TABEL 1: DESIGN REQUIREMENTS
Target Area | Length: W.33rd Ave - W.37th Ave, approx. 900m
Widths: 2.5m (bike path), 2.5m (pedestrian); total 5.0m
Average Maintained Illuminance Levels | ≥5.0 lux (Average Horizontal Illuminance)
≥3.0 lux (Min. Vertical Illuminance at 1.5m)
Average Maintained Uniformity Level (Average/min) | 5:1
Mounting Height | 4.0m - 6.0m (Pole mounted fixture)
1.2m – 1.8m (Bollard configuration)
Pole Spacing | Shall be determined by proponents based on height and lamp output characteristics
Luminaire Style | Option 1 - Pole with arm mounted luminaire. Option 2 - Bollard
TABLE 2: SYSTEM COMPONENTS
Component | Requirements
Complete System (Solar panel, luminaire, | · The system shall be required to provide continuous operation at the required illumination levels outlined in Table 1 for:
pole, battery) | - 14 hours (min.) from November to April
- 10 hours (min.) from May to October
· IP-rated for outdoor environments
· Rated to operate reliably in temperatures from -15°C to +30°C
· CSA, CUL or equivalent approval
· Resistant to vandalism or theft; resilient to dust, moisture accumulation or bird droppings and vibration.
· Surge and Lightning Protection
· System Grounding
· Proponents shall factory test each unit before shipping.
· Product specification sheets with description of performance, dimensions, wiring and installation details to be submitted in the Proposal for review.
Solar Panels/Charging System | · Proponents shall provide number of solar units (as per their design), spacing, part number, dimensions and technical specification of the proposed products with installation and mounting instructions.
· Number and size of panels shall be suited to provide sufficient energy to the battery storage system based on the average sunlight hours available in this location to maintain year-round operability.
· System shall have a readily available port to charge battery storage system from an alternate source. (For example, charging the batteries using AC power source if there is not enough sunlight for solar panels to fully charge batteries if required.)
Luminaire | · LED light source
· 3000K color temperature
· Full Cut-off optics with BUG rating of U-0 (Bollard configurations are exempt, however, up-light shall be kept to a minimum)
· Distribution type 1, 2 or 3
· House Side Shield or equivalent backlight control means available (if required)
· Available dimming control option
· Photometric analysis will be performed with house side shielding on fixtures where residents are in close proximity to luminaire(s).
· "Only target area shall be illuminated, no light trespass into adjacent properties shall be permitted"
· Dark Sky compliant (preferred)
Controller | · "Photocell or timer module capable of activating/deactivating system (manual or remote)"
· Adjustable dimmer control to allow output range of 3-5Lux
Battery | · Battery capacity and output shall be sufficient to provide continuous operation as required in this table; Complete System.
· Proponents shall provide type of battery, ampere-hour rating and other relevant technical specifications.
· Batteries shall come with O&M manual which outlines regular and preventative maintenance required.
· Autonomous battery storage to ensure reliable year round system performance
· Seven (7) consecutive 16 hour nights of energy storage is a required minimum
Pole | · The type and material of pole/bollard shall be clearly specified based on intended design.
· Poles/bollards shall be built and finished suitable for the environment they will be installed (ie: West Coast environment).
· A pole base/bollard drawing which shows anchor bolt pattern that will be required and if there is a need for concrete footing.
· Direct buried installation of the pole/bollard is acceptable provided burial depths and installation instructions are well defined in engineered drawings.
· External loads (wind, snow, vandalism etc) should be considered when selecting the pole/bollard type and installation method.

## Pricing Table
DESIGN
Option 1 - Pole Mounted | [6 empty] | Total ($) | Option 2 - Bollard | [6 empty] | Total ($)
Total Design Costs for Pole Mounted | [6 empty] | 0 | Total Design Costs for Bollard | [6 empty] | 0
FABRICATE, SUPPLY AND DELIVER
| Type/Model number | Quantity | Price | Life cycle (in Years) | Dimensions (cm) | Specs attached in the Proposal? | Total ($) |  | Type/Model number | Quantity | Price | Life cycle (in Years) | Dimensions (cm) | Specs attached in the Proposal? | Total ($)
|  |  | Per unit | [7 empty] | Per unit
Option 1 - Pole Mounted | [7 empty] | Option 2 - Bollard
Solar Light Fixture | [6 empty] | 0 | Solar Light Fixture | [6 empty] | 0
Battery | [7 empty] | Battery
Solar Panel | [7 empty] | Solar Panel
Pole | [7 empty] | Bollard
Charge Controller | [7 empty] | Charge Controller
Delivery | [6 empty] | 0 | Delivery | [6 empty] | 0
( includes shipping and handling) | [6 empty] | 0 | ( includes shipping and handling) | [6 empty] | 0
Innovative feature 1 ( please specify) | [6 empty] | 0 | Innovative feature 1 ( please specify) | [6 empty] | 0
Innovative feature 2 ( please specify) | [6 empty] | 0 | Innovative feature 2 ( please specify) | [6 empty] | 0
Other ( please specify) | [6 empty] | 0 | Other ( please specify) | [6 empty] | 0
Taxes ( please specify) | [6 empty] | 0 | Taxes ( please specify) | [6 empty] | 0
Total Fabricate, Supply and Deliver for Pole base | [6 empty] | 0 | Total Fabricate, Supply and Deliver for Bollard | [6 empty] | 0
INSTALL AND COMMISION
| Type/Model number | Quantity | Price | Life cycle (in Years) | Dimensions (cm) | Specs attached in the Proposal? | Total ($) |  | Type/Model number | Quantity | Price | Life cycle (in Years) | Dimensions (cm) | Specs attached in the Proposal? | Total ($)
|  |  | Per unit | [7 empty] | Per unit
Option 1 - Pole Mounted | [7 empty] | Option 2 - Bollard
Installation, Testing and Commisioning | [6 empty] | 0 | Installation, Testing and Commisioning | [6 empty] | 0
Other ( please specify) | [6 empty] | 0 | Other ( please specify) | [6 empty] | 0
Taxes ( please specify) | [6 empty] | 0 | Taxes ( please specify) | [6 empty] | 0
Total Installation, Testing and Commisioning for Pole Base | [6 empty] | 0 | Total Installation, Testing and Commisioning for Bollard | [6 empty] | 0
Mock up
| Quantity |  |  | Price Per Unit |  |  | Total ($) |  | Quantity |  |  | Price Per Unit |  |  | Total ($)
Option 1 - Pole Mounted | [6 empty] | 0 | Option 2 - Bollard | [6 empty] | 0
Taxes ( please specify) | [6 empty] | 0 | Taxes ( please specify) | [6 empty] | 0
Total Mock up for Pole Base | [6 empty] | 0 | Total Mock up for Bollard | [6 empty] | 0
TOTAL Option 1 Pole Mounted | [6 empty] | 0 | TOTAL Option 1 Bollard | [6 empty] | 0
SUPPORT, OPERATION AND MAINTENANCE – Optional Item
Option 1 - Pole Mounted | [7 empty] | Option 2 - Bollard
| Labour |  | Equipment |  | Material |  | Total ($) |  | Labour |  | Equipment |  | Material |  | Total ($)
Technical Support | [6 empty] | 0 | Technical Support | [6 empty] | 0
Operation and Maintenance | [6 empty] | 0 | Operation and Maintenance | [6 empty] | 0
Other ( please specify) | [6 empty] | 0 | Other ( please specify) | [6 empty] | 0
Taxes ( please specify) | [6 empty] | 0 | Taxes ( please specify) | [6 empty] | 0
Total Support, Operation and Maintenance foe Pole Mounted | [6 empty] | 0 | Total Support, Operation and Maintenance for Bollard | [6 empty] | 0
CHARGE OUT RATES
Proponent should complete the following table setting out the all-inclusive hourly rates for all applicable categories of labour, which rates will then apply pursuant to this project. These rates will only be used for a change of scope that is not within the original scope requested in this RFP.
Job Classification (Please specify) | Regular Rate | Overtime Rate

## Instructions
1. Add rows as needed
2. If bollard option is not available, then clearly state in this in the proposal
3. Proponents are encouraged to submit multiple scenarios and product options available to meet City's requirements specified in the RFP. If there is a variance from the City's requirements, then please specify in the proposal.