## 1. Cover
OFFERED BY
Company Name
PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
REQUEST FOR PROPOSALS PS20210275
Instructions for completing these forms are located on Tab: 2. Instructions.
City of Vancouver Confidential Information
The information contained in this Request for Proposal is confidential and proprietary to the City of Vancouver and is to be used by the recipient solely for the purpose of responding to this RFP. This RFP shall be destroyed or returned to the City of Vancouver upon request.

## 2. Instructions
PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
REQUEST FOR PROPOSALS PS20210275
Completing Appendix 1 - Requirements
1 | Provide company name on Tab 1. Cover in cell highlighted in yellow.
2 | Tab 2. Instructions - These are the instructions for completing Appendix 1
3 | Review Tab 3 & 4 Complete as instructed below
Appendix 1 - Technical Requirements
This Workbook contains multiple Tabs (or Worksheets). Please read the following instructions to ensure that the Proponent completes and/or reviews all the information required for each Tab.
* Please complete ONLY cells highlighted in YELLOW throughout this workbook*
For all "Required" City Conditions please check "Yes" if Proponent can meet the requirements as stated in the "Description" column; also provide the page # in the "Identify All Deviations/Stated Value" column where Proponent demonstrates ability to meet required condition if applicable. For all "Required" City Conditions please check "No" if Proponent cannot meet the requirements as stated in the "Description" column; please include a description of the Proponents proposed deviation from the stated requirements in the "Identify All Deviations/Stated Value" column.
For all "Provide" City Conditions please state Proponents response to the requirement as stated in the "Description" column in the "Proponents Indicative Deviations and Stated Value" column. Provide the page # in the "Bidder Page # Reference" column where Proponent demonstrates ability to meet required condition if applicable.
For all "State" City Conditions please state Proponents response to the requirement as stated in the "Description" column in the "Identify All Deviations/Stated Value" column. Please state any applicable values in the suggested units. Please do not leave any "State" City Conditions blank. If information is unknown or unavailable, please state this in the "Identify All Deviations/Stated Value" column. Provide the page # in the same column where Proponent demonstrates ability to meet required condition if applicable.
For all “Provide” City Requirements, Vendor is to provide the required documentation as described in the “Description” column.
For all "Provide at Delivery" City Conditions please check "Yes" if Proponent can meet the requirements as stated in the "Description" column or "No" if Proponent cannot meet the requirements as stated in the "Description" column. If "No" please include a description of the Proponents proposed deviation from the stated requirements in the "Proponents Indicative Deviations and Stated Value" column. Provide the page # in the "Bidder Page # Reference" column where Proponent demonstrates ability to meet required condition if applicable.
For all "Optional" City Conditions please check "Yes" if Proponent can meet the requirements as stated in the "Description" column or "No" if Proponent cannot meet the requirements as stated in the "Description" column. If "No" please include a description of the Proponents proposed deviation from the stated requirements in the "Proponents Indicative Deviations and Stated Value" column. Provide the page # in the "Bidder Page # Reference" column where Proponent demonstrates ability to meet required condition if applicable.
For all "Preferred" City Conditions please check "Yes" if Proponent can meet the requirements as stated in the "Description" column; also provide the page # in the "Bidder Page # Reference" column where Proponent demonstrates ability to meet preferred condition if applicable. For all "Preferred" City Conditions please check "No" if Proponent cannot meet the requirements as stated in the "Description" column; please include a description of the Proponents proposed deviation from the stated requirements in the "Proponents Indicative Deviations and Stated Value" column

## 3. General
PS20210275 - PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
Specifications and Documentation:
Supplier's Name:________________________________________ |  | Make & Model of Proposed Equipment:__________________________________________
| Description | City Conditions | Compliance Yes / No | Identify All Deviations / Stated Values
Hardware: DCFC, Level 2
| CSA, cUL or other recognized certification approved for use in Canada. | Required | Please Choose
Safety compliance with:
| - Underwriters Laboratories of Canada (ULC) | Required | Please Choose
| - Canadian Standards Association (CSA) | Required | Please Choose
At a minimum:
| - One year warranty | Required | Please Choose
| - 24/7 customer support call centre | Required | Please Choose
| Ability to power cycle at charger (not just at breaker). | Preferred | Please Choose
| Weatherproof to minimum of NEMA 3R. | Required | Please Choose
| Ability to operate in a temperatures range of -30C to 50C. | Required | Please Choose
| Over-current protection that prevents circuit breaker trips | Required | Please Choose
| Wall-mounted with mounting hardware provided. | Required | Please Choose
| Length of charging cord included. | Provide
| Estimated life of equipment in indoor and outdoor (Vancouver) settings. | Provide
Load Sharing
| Load Sharing: EVSE should have the ability to manager multiple stations under a single load threshold, either at a circuit or a panel level. | Required | Please Choose
| Description of what is offered. | Provide
Network Services
Hardware communications protocol within the DCFC and Level 2 must integrate with selected network management platform. The following information and controls must be available from the EV charging station to the Network Operations Centre:
| - EV Charging station status | Required | Please Choose
| - Error messages | Required | Please Choose
| - Control functions | Required | Please Choose
| - Operating data | Required | Please Choose
| - EV charging station status | Required | Please Choose
| Supports remote firmware upgrades | Required | Please Choose
| Supports remote power cycling | Required | Please Choose
| Data access: off-site database shall be accessible to a City administrator via a web browser. Website shall provide historical data, real time usage and status information. | Required | Please Choose
Data reporting to a City network administrator must include at a minimum:
| - Session details that include time-of-day for session start and stop, connected time, active charging time, kWh delivered, session completion description (i.e. – ended by user, charging complete, station fault, etc). | Required | Please Choose
| - Station-by-station utilization | Required | Please Choose
| - Total up-time per station | Required | Please Choose
| Proponent is responsible for enabling cellular DCFC connectivity to a data network prior to shipping the unit(s). | Required | Please Choose
| For open network protocol providers, compliance with all of Open Charge Point Protocol (“OCPP”, minimum v.1.6), Open Charge Point Interface (“OCPI”, minimum v.2.1.1). | Preferred | Please Choose
| Must automatically continue to provide a charge to the EV if station loses network connectivity or if remote station management system is offline. | Required | Please Choose
| In the event of a power module failure, the unit must automatically reconfigure to provide a charge at a reduced power level | Required | Please Choose
| Description of location requirements to support network connection (e.g. cellular, Wi-Fi, or other connectivity) | Provide
| Itemized costs associated with data transfer, collection, and access. Please specify whether costs are one-time and/or on-going (with rate). | Provide
Security and Access Control
| Security - Model offered shall come with a secure means of allowing only authorized users access and/or vehicles to be charged (ie. RFID card) | Required | Please Choose
| Description of how user and/or vehicle is identified/authorized by charging station. Please include any costs for identification methods (i.e.. Cost per RFID card) | Provide
Installation Services
| Utilizes only electrical contractors licensed within the Province of BC | Required | Please Choose
| All work to be completed under appropriate permit and installation to meet Canadian electrical code requirements. | Required | Please Choose
Standard Documentation
| Estimated life of equipment in indoor and outdoor (Vancouver) settings. | Required | Please Choose
| Data sheets of models offered | Required | Please Choose
| Metering: Provide the specifications for any electrical metering included with your hardware. Indicate if you offer stations with Measurement Canada certified meters. | Required | Please Choose
| Provide mounting instructions. | Required | Please Choose
| Provide wiring and installation diagrams. | Required | Please Choose
| Standard warranty document | Required | Please Choose

## 3. EV Chargers - Level 2
PS20210275 - PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
Specifications and Documentation:
Supplier's Name:________________________________________ |  | Make & Model of Proposed Equipment:__________________________________________
| Description | City Conditions | Compliance Yes / No | Identify All Deviations / Stated Values
Overview
| Make and model of unit(s) offered. | Provide
| Data sheets of model offered. | Provide
Technical Specifications
Hardware: Level 2 (standard)
| Output Voltage - Rated voltage shall be up to 240VAC. | Required | Please Choose
| Output Current - Rated current of 32A. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage - Unit offered shall accept 208-240VAC at 50-60Hz. | Required | Please Choose
| Input Current - Unit offered shall accept a maximum of 40A. | Required | Please Choose
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) J1772 standard "Electric Vehicle and Plug In Hybrid Electric Vehicle Conductive Charge Coupler" | Required | Please Choose
Hardware: Level 2 (high output)
| Output Voltage - Rated voltage shall be up to 240VAC. | Required | Please Choose
| Output Current - Rated current of 40A. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage - Unit offered shall accept 208-240VAC at 50-60Hz. | Required | Please Choose
| Input Current - Unit offered shall accept a maximum of 40A. | Required | Please Choose
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) J1772 standard "Electric Vehicle and Plug In Hybrid Electric Vehicle Conductive Charge Coupler" | Required | Please Choose
Multiple Ports
| Charger with multiple ports available. | Preferred | Please Choose
| Number of ports available per charger. | Provide
Standard Documentation
| Estimated life of equipment in indoor and outdoor (Vancouver) settings. | Required | Please Choose
| Data sheets of models offered | Required | Please Choose
| Metering: Provide the specifications for any electrical metering included with your hardware. Indicate if you offer stations with Measurement Canada certified meters. | Required | Please Choose
| Provide mounting instructions. | Required | Please Choose
| Provide wiring and installation diagrams. | Required | Please Choose
| Standard warranty document | Required | Please Choose

## 3. EV Chargers - DCFC
PS20210275 - PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
Specifications and Documentation:
Supplier's Name:________________________________________ |  | Make & Model of Proposed Equipment:__________________________________________
| Description | City Conditions | Compliance Yes / No | Identify All Deviations / Stated Values
Overview
| Make and model of unit(s) offered. | Provide
| Data sheets of model offered. | Provide
Technical Specifications
Hardware: DCFC #1
| Output Voltage: no minimum DC voltage. | Required | Please Choose
| Output Power: minimum 50 kW. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage. | Provide
| Input Current. | Provide
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) Combined Charging System (CCS) | Required | Please Choose
Hardware: DCFC #2
| Output Voltage: minimum 900 VDC. | Required | Please Choose
| Output Power: minimum 50 kW. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage. | Provide
| Input Current. | Provide
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) Combined Charging System (CCS) | Required | Please Choose
Hardware: DCFC #3
| Output Voltage: no minimum DC voltage. | Required | Please Choose
| Output Power: approximately 25 kW. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage. | Provide
| Input Current. | Provide
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) Combined Charging System (CCS) | Required | Please Choose
Hardware: DCFC #4
| Output Voltage: minimum 900 VDC. | Required | Please Choose
| Output Power: approximately 25 kW. | Required | Please Choose
| Rated Voltage. | Provide
| Rated Current. | Provide
| Output in kW. | Provide
| Input Voltage. | Provide
| Input Current. | Provide
| Requirements of upstream electrical circuits. | Provide
| Connector compliance with Society of Automotive Engineers (SAE) Combined Charging System (CCS) | Required | Please Choose
Standard Documentation
| Estimated life of equipment in indoor and outdoor (Vancouver) settings. | Required | Please Choose
| Data sheets of models offered | Required | Please Choose
| Metering: Provide the specifications for any electrical metering included with your hardware. Indicate if you offer stations with Measurement Canada certified meters. | Required | Please Choose
| Provide mounting instructions. | Required | Please Choose
| Provide wiring and installation diagrams. | Required | Please Choose
| Standard warranty document | Required | Please Choose

## 4. Options
PS20210275 - PROVISION OF CITY FLEET ELECTRIC VEHICLE CHARGING INFRASTRUCTURE, MAINTENANCE, AND SUPPORT
Options
Supplier's Name:________________________________________
| Description | City Conditions | Compliance Yes / No | Identify All Deviations / Stated Values
Options
The City of Vancouver would like information on optional equipment that may be selected in addition to or in place of those specified in Item 1.
Option 1
| Extended Warranty | Optional | Please Choose
| Description of what is offered. | State
| Details of manufacturer's extended warranty. | State
| Limitations / Exclusions from manufacturer's extended warranty | State
Option 2
| Load Management options available. | Optional | Please Choose
| Detailed description of what is offered. | State
Option 3
| Pedestal mounting options available. | Required | Please Choose
Provide
Option 4
| Charging cord length options available. | Required | Please Choose
Provide
Option 5
| Cable management options available. | Required | Please Choose
Provide
Option 6
|  | Required | Please Choose
Provide